## common
Variables | Description | Data type
enum_MGCC_StaMach | MGCC state machine | enumeration
enum_PV_LC_StaMach | PV local controller state machine | enumeration
enum_Batt_LC_StaMach | Battery local controller state machine | enumeration
enum_BakGen_LC_StaMach | Backup generator local controller state machine | enumeration
enum_IntRupt_StaMach | IntelliRupter state machine | enumeration

## PV
Variables | Description | Data type
i_PV_PF_cmd | Power factor | integer
f_PV_Curr | Curtailment | float
f_PV_Ramp | Ramp rate | float
f_PV_Act_delay | Action delay | float
f_PV_Random | Randomization | float
i_PV_Fault | Fault code (according to fault table) | integer
i_PV_Warning | Warning code (according to warning table) | integer
f_PV_Temperature | Local Controller Temperature | float
f_PV_Vol | Terminal voltage, RMS value | float
f_PV_Freq | Terminal frequency | float
f_PV_P | Output power | float
f_PV_Q | Output reactive power | float
f_PV_PowFct | Power factor of PV inverter | float
i_PV_Q_Mode | Reactive Power Mode (Constant Q=0 Constant PF=1, Control V=2) | integer
b_PV_Ena | Remote enable/disable | binary

## Battery
Variables | Description | Data type
i_Batt_Warning | Warning code (according to warning table) | integer
f_Batt_Temperature | Local Controller Temperature | float
f_Batt_Vol | Terminal voltage, RMS value | float
f_Batt_Freq | Terminal frequency | float
f_Batt_P | Output power | float
f_Batt_Q | Output reactive power | float
f_Batt_SOC | State of Charge | float
i_Batt_Q_Mode | Reactive Power Mode (Constant Q=0 Constant PF=1, Control V=2) | integer

## BackupGenerator
Variables | Description | Data type

## IntelliRupter
Variables | Description | Data type
b_IntRup_PhaAPos | Pole A position, 1 open, 0 closed | binary
b_IntRup_PhaBPos | Pole B position, 1 open, 0 closed | binary
b_IntRup_PhaCPos | Pole C position, 1 open, 0 closed | binary
b_IntRup_PhaABCPos | Pole ABC position, 1 open, 0 closed | binary
b_IntRup_GoodVolSrc_X | Good voltage source at terminor X, 1 good, 0 not good | binary
b_IntRup_GoodVolSrc_Y | Good voltage source at terminor Y, 1 good, 0 not good | binary
f_IntRup_Vol_AX | primary phaseA-to-ground voltage magnitude X side, RMS value | float
f_IntRup_Vol_BX | primary phaseB-to-ground voltage magnitude X side, RMS value | float
f_IntRup_Vol_CX | primary phaseC-to-ground voltage magnitude X side, RMS value | float
f_IntRup_Vol_AY | primary phaseA-to-ground voltage magnitude Y side, RMS value | float
f_IntRup_Vol_BY | primary phaseB-to-ground voltage magnitude Y side, RMS value | float
f_IntRup_Vol_CY | primary phaseC-to-ground voltage magnitude Y side, RMS value | float
f_IntRup_Curr_A | Phase A current, RMS value | float
f_IntRup_Curr_B | Phase B current, RMS value | float
f_IntRup_Curr_C | Phase C current, RMS value | float
f_IntRup_P_A | Phase A active power | float
f_IntRup_P_B | Phase B active power | float
f_IntRup_P_C | Phase C active power | float
f_IntRup_P_ABC | total active power | float
f_IntRup_Q_A | Phase A reactive power | float
f_IntRup_Q_B | Phase B reactive power | float
f_IntRup_Q_C | Phase C reactive power | float
f_IntRup_Q_ABC | total reactive power | float
f_IntRup_S_ABC | total kVA of phsae ABC | float
f_IntRup_PowFct_A | Phase A power factor | float
f_IntRup_PowFct_B | Phase B power factor | float
f_IntRup_PowFct_C | Phase C power factor | float
f_IntRup_PowFct_ABC | total power factor | float
f_IntRup_THD_Vol_AX | total Harmonic distortion at phase A voltage, X side | float
f_IntRup_THD_Vol_BX | total Harmonic distortion at phase B voltage, X side | float
f_IntRup_THD_Vol_CX | total Harmonic distortion at phase C voltage, X side | float
f_IntRup_THD_Vol_AY | total Harmonic distortion at phase A voltage, Y side | float
f_IntRup_THD_Vol_BY | total Harmonic distortion at phase B voltage, Y side | float
f_IntRup_THD_Vol_CY | total Harmonic distortion at phase C voltage, Y side | float
f_IntRup_THD_Curr_A | total Harmonic distortion at phase A current, X side | float
f_IntRup_THD_Curr_B | total Harmonic distortion at phase B current, X side | float
f_IntRup_THD_Curr_C | total Harmonic distortion at phase C current, X side | float
f_IntRup_Fre_X | frequency, X side | float
f_IntRup_Fre_Y | frequency, Y side | float
f_IntRup_DelFreq | the difference in frequency between X and Y | float
f_IntRup_VolAng_AX | Phase A voltage angle, X side | float
f_IntRup_VolAng_BX | Phase B voltage angle, X side | float
f_IntRup_VolAng_CX | Phase C voltage angle, X side | float
f_IntRup_VolAng_AY | Phase A voltage angle, Y side | float
f_IntRup_VolAng_BY | Phase B voltage angle, Y side | float
f_IntRup_VolAng_CY | Phase C voltage angle, Y side | float

## PV_LC
Variables | Description | Data type
b_PV_Prio | Power / Reactive Power priority (Power=0, Reactive Power=1) | binary
b_PV_MPPT | MPPT or Power curtailment (MPPT=0, Power curtailment=1) | binary
b_PV_Curtail_Mode | Curtailment Mode (Percentage=0, Absolute value=1) | binary
b_PV_Status | Status of PV inverter | binary
i_PV_Status_Cmd | Operating state (according to state machine) | integer
i_PV_Vol_cmd | Terminal voltage command for Control V mode | integer
f_PV_P_cmd | Output power curtail command (absolute value) | float
f_PV_P_percent | Output power curtail command (percentage) | float
f_PV_Q_cmd | Output reactive power command | float
f_PV_Q_PF_cmd | Output power factor command 1 unit indicates 0.001 | float
i_PV_Q_Mode_cmd | Reactive power mode command (Constant Q=0 Constant PF=1, Control V=2) | integer
f_PV_P_lim | Output power limit | float
f_PV_Q_lim | Output reactive power limit | float
f_PV_P_ramp | Output power ramp rate | float
f_PV_Q_ramp | Output reactive power ramp rate | float
b_PV_Fault_Clr | Clear faults, warnings are not affected | float
b_PV_Warning_Clr | Clear warnings, faults are not affected | float
b_PV_Prio_cmd | Power / Reactive Power priority command (Power=0, Reactive Power=1) | binary
b_PV_MPPT_cmd | MPPT or Power curtailment command (MPPT=0, Power curtailment=1) | binary
b_PV_Curtail_Mode_cmd | Curtailment mode command (Percentage=0, Absolute value=1) | binary

## Battery_LC
Variables | Description | Data type
b_Batt_IE | Inertia Emulation Function Enable (Disable=0, Enable=1) | binary
b_Batt_Prio | Power / Reactive Power priority(Power=0, Reactive Power=1) | binary
i_Batt_Fault | Fault code (according to fault table) | integer
i_Batt_Status_Cmd | Operating state (according to state machine) | integer
i_Batt_Vol_cmd | Terminal voltage command for islanded operation and control V mode | integer
f_Batt_Freq_cmd | Terminal frequency command for islanded operation | float
f_Batt_P_cmd | Output power command | float
f_Batt_Q_cmd | Output reactive power command | float
f_Batt_Q_PF_cmd | Output power factor command 1 unit indicates 0.001 | float
i_Batt_Q_Mode_cmd | Reactive power mode command (Constant Q=0 Constant PF=1, Control V=2) | integer
f_Batt_P_lim | Output power limit | float
f_Batt_Q_lim | Output reactive power limit | float
f_Batt_P_ramp | Output power ramp rate | float
f_Batt_Q_ramp | Output reactive power ramp rate | float
b_Batt_Fault_Clr | Clear faults, warnings are not affected | binary
b_Batt_Warning_Clr | Clear warnings, faults are not affected | binary
b_Batt_IE_cmd | Inertia emulation function enable command (Disable=0, Enable=1) | binary

## BackupGen_LC
Variables | Description | Data type

## MGCC
Variables | Description | Data type
b_Req_Conn_MGCC | MGCC sends request to DMS/SCADA for reconnection | binary
b_Req_Disconn_MGCC | MGCC sends request to DMS/SCADA for disconnection | binary
b_Resp_Conn_req_DMS | MGCC sends response to reconnection request, requested by DMS/SCADA | binary
b_Resp_Disconn_req_DMS | MGCC sends response to disconnection request, requested by DMS/SCADA | binary
b_Reclose_Ena | Reclosing enable signal | binary
b_Req_Conn_DMS | DMS/SCADA sends request to MGCC for reconnection | binary
b_Req_Disconn_DMS | DMS/SCADA sends request to MGCC for disconnection | binary
b_Resp_Conn_req_MGCC | DMS/SCADA sends response to reconnection request, requested by MGCC | binary
b_Resp_Disconn_req_MGCC | DMS/SCADA sends response to disconnection request, requested by MGCC | binary
b_Events_ABN | Internal event parameter | binary
b_Events_BKS | Internal event parameter | binary
b_Events_FLT | Internal event parameter | binary
b_Events_G2I_IN | Internal event parameter | binary
b_Events_G2I_UN | Internal event parameter | binary
b_Events_GC | Internal event parameter | binary
b_Events_I2G | Internal event parameter | binary
b_Events_ISD | Internal event parameter | binary
b_Events_OFF | Internal event parameter | binary
b_Events_STD | Internal event parameter | binary
string